Error: Reference source not found

Table of Contents

1	Scope of Application	3

2	Purpose	3

3	Definitions	3

4	Referenced Documents	3

5	Responsibility and work flow	4

5.1	Responsibility	4

5.2	Storage categories	4

5.3	Procedure	4

6	Documentation and Quality-Records	8

7	Amendments	8

8	Distribution	8

# Scope of Application

This work instruction applies to the storage and protection of equipment and materials at construction sites.

# Purpose

This work instruction describes the minimum requirements for product specific storage of equipments as well as actions for the recognition and prevention of corrosive and mechanical damage.

# Definitions

| CLIENT | The company who awarded the contract to Linde LE |
| --- | --- |
| COMPANY | Linde Engineering Division, hereinafter referred to as "COMPANY", who manages and monitors all construction and erection activities that are within its scope of the contract and usually procures all the required equipment, materials and services |
| CONTRACTOR | The company being engaged by COMPANY for the execution of all material management and warehousing activities according to the purchase order and the related scope of work for these services |
| Equipment | This term refers to all items such as apparatus, machinery, package units - procured and delivered by COMPANY or third party. |
| SSI | Site Superintendent |
| Materials | This term refers to sheet metal, piping materials, semi-finished products, electrical materials, instrumentation materials, cables and spare parts, etc. - procured and delivered by COMPANY |
| OS&D | Report for Overages, Shortages, Non-Conformities and Damages, as well for the definition of corrective measures |
| TPS | Technical Purchase Specification |

# Referenced Documents

  - Manufacturer / Vendor specifications

  - Project specific specifications and regulations such as preservation specifications and HSE Program Site

  - LS 148-05	Protective Measures for Transportation

  - &AA-W-DW 0803 	Overage, Shortage and Damage Report (OS&D)

  - &AA-W-SC 0801  	Material Receiving, Inspection, Release and Site Procurement 		for Equipment and Materials

  - &AA-W-SC 0820	Preservation Procedure

# Responsibility and work flow

## Responsibility

The warehouse personnel as well as the SSI Material Administration of COMPANY are responsible to carry out and to monitor the specified specifications and procedures.

The SSI Material Administration of COMPANY monitors compliance with this work instruction.

COMPANY'S responsibility commences on arrival of the goods at the construction site and ends with their issue for use to the CONTRACTOR.

Storage and specific measures for special equipment such as apparatus, machines, and sensitive electronic components have to be agreed with the respective responsible SSI and recorded in the preservation specification.

## Storage categories

max. +26°C

## Procedure

### General storage conditions

In general, storage of all types of equipment has to be done in accordance with the supplier / manufacturer regulations. If no specific regulations have been issued by the supplier / manufacturer, the following minimum requirements have to be observed:

- The storage area subsoil has to be sealed or compacted in accordance with the storing requirements of the parts to be stored (e.g. finished concrete slabs, asphalt, compacted gravel).

- The storage areas should be leveled, dry and protected from flooding.

- Storage markings according to international standards (e.g. store only in closed rooms) as well as special storage conditions (e.g. storage temperature) have to be observed.

- Parts stored outdoor shall not be laid directly on the ground. They have to be stored on wooden beams, boards or palettes.

- Parts packed in boxes approved for outdoor storage have to be protected against sand, rain, snow and high humidity by being covered with a watertight tarpaulin or foil, or stored in a sheltered area.

- The equipment parts have to be stored and arranged distinctly in groups of equipment type (e.g. apparatus, machines, piping etc.) and to be identified clearly with the relevant designation (e.g. Equipment No.).

- Checked and unchecked components as well as damaged and defect parts have to be clearly marked and stored clearly separated from each other.

- The number of persons authorized to access the storage areas (excluding warehouse personnel) have to be kept at the minimum and names have to be recorded.

- Material for Oxygen Service shall be stored in a segregated area, clearly marked OXYGEN SERVICE. If not already marked by supplier, valves shall be tagged with a durable label fixed to the hand wheel and marked OXYGEN SERVICE. During storage and handling of above mentioned material, any further contamination shall be prevented.

### Product specific storage

The following notes are the minimum requirements per international standards, but nevertheless do not replace product specific supplier / manufacturer regulations.

#### Piping material

Materials subject to indoor storage (Storage category 4)

- All piping parts (flanges, fittings) < 3"

- Valves < 3"

- Safety valves

- Screws, bolts, nuts, gaskets, other small parts.

Materials that can be stored outdoor

- All pipes (Storage category 1)

- Flanges, fittings, etc.) > 3" (Storage category 2)

- All supports (Storage category 2)

- Supports (excluding wooden parts), sheet metal, steel structures. (Storage category 1)

Valves

Valves have to be stored in the “closed” position and the flange openings covered with a plastic cap (alternatively with watertight foil).

Actuators and bare spindles have to be covered with foil.

Valve stems must be kept in a vertical position.

Piping material

Pipes, fittings and other parts with curved surfaces, stored outside, have to be laid down in a position so that rainwater and condensate can drain off.

Pipes have to be secured with wedges to prevent slipping. The stacked height should not be more than 2 meters. The stack has to be arranged in a pyramid shape.

Storage of cement-lined and / or PE-coated pipes:

- Store on solid wooden planks, not on steel (minimum 3 supports per 12 meter length)

- For diameters < DN 800 mm, a maximum of 2 layers on top of each other, with wooden planks in between, is allowed

- For diameters > DN 800 mm, only a single layer storage is permitted.

Supports and steel structure parts have to be stored so that damage to threads and coatings is avoided. Arched or funnel-shaped surfaces have to be stored so that accumulation of rainwater, condensate etc. cannot occur.

After unpacking, the parts have to be marked clearly to avoid mix-ups (checked vs. not checked). After control of received materials, they have to be arranged and stored distinctly according to their size, pressure rating and material in designated shelves and zones.

Stainless and non-stainless steels have to be stored clearly separated from each other.

Flange sealing faces and machined parts may not be used for marking purposes.

Gaskets

- Leave as long as possible in the original packaging – highly sensitive to humidity.

- Stack-up not more than 20 pieces of unpacked gaskets – surfaces are very sensitive, i.e. easy to scratch.

- Gaskets must not be hung up – can bend / buckle and break easily.

#### Electrical and Instrument equipment and materials

In general, storage guidelines specified by the supplier / manufacturer shall apply.

Storage in dry and heated halls is obligatory. (Storage category 4)

Exceptions, means outdoor storage Storage category 1, apply only to:

- Instrumentation and Electrical cable drums, if the ambient temperature does not exceed the range between -60 °C and +50 °C. (stored at an ambient temperature of < + 5 °C, the cables could require pre-warming in an interim storage area (hall) prior to being installed, clarify with SSI Electrical and Instrumentation of COMPANY whether pre-warming is required)

- Cable trays, Supports E & I (e.g. in Container)

- Motors, transformers and junction boxes designed for outdoor installation.

- Analyzer Shelter.

Exceptions, Storage category 5 (temperature-controlled >+5/<26°C) shall only apply to:

- DCS/PLC/Control room Equipment

- Cables for control room

- Substation Equipment

- Control valves

- Sensible E&I Equipment which require temperature-controlled starage

- PC’s & IT Equipment

Large and pre-fabricated components should preferably be kept in their original packing (boxes) until start of installation. However, they have to undergo a material receiving and controlling to avoid damages and to ensure completeness.

Equipment, accessories and assembly materials have to be stored in zones or on shelves marked clearly with the type of item (transmitter, manometer, switch etc.).

#### Stationary and Rotating Equipment

In general, storage guidelines specified by the supplier / manufacturer apply.

Outdoor storage is usually permitted. For machines (e.g. compressors, pumps), however, suitable weather protection (Storage category 4) has to be provided.

If possible, items (e.g. column trays) packed in boxes have to be kept in their original packing until start of installation. In amber time, before start of installation, the packing shall be controlled for completeness and checked against the drawings.

Equipment accessories, e.g. spare gaskets, manhole screws, anchor bolts etc. have to be stored in closed rooms and marked clearly with their respective equipment no.

Shafts of big machines (e.g. turbo compressors, turbines) have to be stored according to the manufacturer’s specifications, e.g. intermediate bridge bearing against sagging.

#### Chemicals, filling materials, hazardous materials

These materials have to be generally stored in dry and closed rooms with temperature control (Storage category 5)

Hazardous materials have to be kept in a zone separate from the other items. The containers (e. g. barrels, bags) have to be marked clearly with the name of the substance and its correct hazardous class symbol. Hazardous material data specifications have to be available and to be observed.

"No Smoking" signs and a sufficient number of fire extinguishers have to be provided in the hazardous storage area.

National and local regulations have to be observed. For further information refer to "HSE Program Site".

### Preservation measures

#### General notice

The supplier / manufacturer shall provide protection against mechanical damage and corrosion for all the equipment procured by COMPANY or by third parties, both during transport and also for the limited duration of storage at the construction site. COMPANY'S minimum requirements concerning type, extent and duration of the protection measures are specified in the terms of TPS. In addition, equipment-specific regulations of the supplier / manufacturer have to be observed.

#### Preservation after transport

- Check existing temporary corrosion protection (for details refer to LS 148-05 - Preservation Procedure).

- Visual inspection for damage, closure of all openings and salt residues is necessary.

- Check pressure indication of apparatus filled with nitrogen; if non-pressurized, open and inspect according to safety regulations for corrosion defects. In the following, seal leakage areas and refill with nitrogen at 0.2 bar, if an immediate integration into the plant does not occur. After the opening of boxes / containers a visual inspection (spot check) of the parts are necessary for: corrosion damage, salt residues, intact foil packaging and color change of desiccants.

- Salt residues, if necessary, have to be removed from ferrous steel equipment (scrub, rinse with potable water).

- In general, equipment made of aluminum and austenitic stainless steel that has been transported unpacked by sea, is to be rinsed / scrubbed carefully with water (max. chloride content of 25 ppm) and any salt residue is to be removed out of corners and crevices.

- Inspection of cable ends. Cable ends have to be closed with a watertight plastic tape to prevent entry of water.

#### Storage related activities

- Protect equipment and materials against rain and other weather effects; avoid build-up of condensation and mechanical damage by compliance with product specific storage conditions (sections 5.3.1 – 5.3.4).

- Regular inspection of the protection, e.g. intact foil covers, is necessary.

- Periodic inspection, and if required, renewal of temporary corrosion protection, e.g. condition of the strip lacquer, desiccant, etc. is necessary.

- Special supplier / manufacturer regulations, e.g. turning of motor shafts, piston engines, shall be strictly complied with.

For equipment kept in the original package, measures have to be taken latest after the specified protection period (from the delivery date onwards) to guarantee continued protection of the goods. Thereby the project specific preservation specifications have to be obtained.

### Organizational measures

If no protective actions or inadequate measures have been taken by the supplier / manufacturer in respect of corrosion and mechanical damage, this fact has to be recorded in an OS&D.

Any kind of damage caused by transport, storage etc. has to be recorded in an OS&D (&AA-W-DW 0803 Overage, Shortage and Damage Report (OS&D)).

COMPANY has to define subsequent improvements and corrective actions concerning repair of Non Conformity and damages and clarify solutions with the supplier / manufacturer.

# Documentation and Quality-Records

The SSI Material Administration of COMPANY collects and archives:

- All storage, protection, and preservation regulations

- Overage, Shortage & Damage Report (OS&D).

# Amendments

Amendment recommendations shall be sent in writing to the Process Owner or Reference Process Manager responsible for the process step.

# Distribution

This procedure is not subject to any confidentiality requirements and is available for employees of The Linde Group or external parties with legitimate interests.

The Reference Process Manager allocates the access rights in Documentum and is responsible for the distribution and publication of this work instruction.