## Slide 1
 | PROJECT KENT DCS Architecture Drawing | 
© 2020 Air Products and Chemicals, Inc. All information herein is the property of Air Products unless another source is shown. This document is classified as Air Products Internal Use Only is subject to return on demand and must not be disclosed or reproduced without prior written consent. This information may be subject to export controls. Disclosure contrary to U.S. law is prohibited.
50034819-PCE-DD2-00001
Revision 0
02 July 2024

## Slide 2: COMMON ARCHITECTURE ICONS
RACK NAME
PDC Building
Customer Supplied Control Building
BUILDINGS/ROOMS/CONTAINERS
DCS cabinet
(remote I/O, PLC,
etc)
CPU
SERVER
AP Network Firewall
Switch
IO RACK
XXUSxxxx##xSxS
Engineering/Operator Station
Dual/Single Monitor
DCS Architecture
Project Name: Project Kent
Rev.
Date
By
Chk
Description
0
02 Jul 24
VJ
App
KEY
3RD PARTY (KVM)
TERMINAL BUS
SYSTEM BUS
I/O BUS
Solid Line: Copper; Dotted Line: Fiber
PRINTER
I/O Bus OLM
KVM
CLIENT

## Slide 3
PCoIP
ASU CPU
(Simplex)
PCoIP
OS
Single Station
Customer Supplied Control Building
Engineering
Station
KEY
(PCoIP)
TERMINAL BUS
SYSTEM BUS
I/O BUS
FO Patch
Panel
ProfiNet
ProfiNet Service Bridge
ProfiNet
Security module
SCALANCE “S”
I/O BUS
ProfiNet
Bridge BUS
ProfiNet
I/O BUS
Profibus
Fiber
Optic
DCS Architecture
Project Name: Project Kent
Rev.
Date
By
Chk
Description
0
02 Jul 24
VJ
App
Analyzers
Notes:
Overall Cyber security responsibility with customer.
It is considered that analyser panels will be supplied by AP (Indoor Installation) which will be installed in Customer supplied building.
Presently 16 signals (4 AI, 4 AO, 4 DI and 4 DO) are considered as interface between Customer and ASU plant. All interfaces are hardwired. The identification of the actual tags/signals to be finalised during detailed engineering. Serial Interface is not considered in present estimate.
It is considered that Customer supplied building will have Controller/CPU panel, Cryo area RIO panels and hardwired trip panels situated. Other RIO panels will be placed in field for respective sections.
It is considered that Telecom/Fire and Gas system is in Customer scope i.e. Engineering, supply and installation of the Telecom/Fire and Gas system is by Customer.

## Slide 4
Simplex
CPU
Analyzer Profibus
Network Switches
& Servers
System Bus
Scalance Switch
ASU
ESD cabinet
Hardwired SIS
CPU Cabinet
FO
FO
FO
BA 2xRJ45
Bus adapter
Cu
SCALANCE
XF204-2BA
1-BA 2xRJ45
1- BA 2xSCRJ
ET 200SP HA
ET 200SP HA
ET 200SP HA
Single IM with
BA 2xSCRJ
Bus adapter
Single IM with
BA 2xSCRJ
Bus adapter
Single IM with
BA 2xSCRJ
Bus adapter
Multimode Fiber Optic
ASU I/O Bus
ProfiNet Service Bridge
DCS Architecture
Project Name: Project Kent
Rev.
Date
By
Chk
Description
0
02 Jul 24
VJ
App
Customer Supplied Control Building
I/O
Cabinet Compression Section
I/O
Cabinet Cryo Section
I/O
Cabinet Front End Section
I/O
Cabinet PDC (MCC Interface)
PDC Building
Field